## Sheet1
Availability | Peak Load | CFE | Location | Solar Capacity | Bess Capacity | Wind Capacity | HD - 7F.05 - simple cycle #Units | HD - 7HA.02 - simple cycle #Units | LM2500+G4 - simple cycle #Units | LM25200 22MW - simple cycle #Units | HD - 7F.05 - combined cycle #Units | HD - 7HA.02 - - combined cycle #Units | LM2500+G4 - combined cycle #Units | LM25200 22MW - combined cycle #Units | Solar Utilisation | Bess Utilisation | Wind Utilisation | HD - 7F.05 - simple cycle Utilisation | HD - 7HA.02 - simple cycle Utilisation | LM2500+G4 - simple cycle Utilisation | LM25200 22MW - simple cycle Utilisation | HD - 7F.05 - combined cycle Utilisation | HD - 7HA.02 - - combined cycle Utilisation | LM2500+G4 - combined cycle Utilisation | LM25200 22MW - combined cycle Utilisation | Installed Capacity | Availlability | LCOE | CFE | Carbon Intensity | Solar Curtainlment | Wind Curtailment
99.9923 | 1000 | 60 | High Solar Low Wind |  |  |  | 2

## Sheet2
| Availability | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
| Peak Load | 1350 | 1350 | 1350 | 1350 | 1350 | 1350 | 1350 | 1350
| CFE | 69% | 70.8% | 70.47% | 70.09% | 80.41% | 79.65% | 81.18%
| Location | High Solar High Wind | High Solar Low Wind | Low Solar High Wind | Low Solar Low Wind | High Solar High Wind | High Solar Low Wind | Low Solar High Wind | Low Solar Low Wind
| Solar Capacity (#Units) | 0.8 | 1.3 | 1.2 | 1.8 | 1.1 | 1.6 | 1.6
| Bess Capacity (#Units) | 18 | 22 | 15.1 | 25 | 18.5 | 60 | 30
| Wind Capacity (#Units | 1.1 | 0 | 1.6 | 0.9 | 1.3 |  | 1.7
CT—industrial frame | HD - 7F.05 - simple cycle (#Units) | 3 | 4 | 3 | 4 | 3 | 3 | 3
Was not included in study | HD - 7HA.02 - simple cycle (#Units) | 0
| LM2500+G4 - simple cycle (#Units) | 0
| LM25200 22MW - simple cycle (#Units) | 0
Was not included in study | HD - 7F.05 - combined cycle (#Units) | 0
CC—single-shaft | HD - 7HA.02 - - combined cycle (#Units) | 1 | 1 | 1 | 1 | 1 | 1 | 1
| LM2500+G4 - combined cycle (#Units) | 0
| LM25200 22MW - combined cycle (#Units) | 0
IC | Interntal Combustion (#Units) | 0 | 2 |  |  |  | 1.6
| CT_35MW (#Units) - comparable LM2500 | 0
CT_16MW | CT_16MW (#Units) - no comparable in GE fleet. - | 6 | 2 | 3 |  | 6 | 3 | 3
| Solar Capacity Capacity Built (MW) | 1976.3 | 3117.9 | 2813.7 | 4374.9 | 2813.7 | 3952.6 | 3952.6 | 2470.375 | 2398.3846 | 2344.75 | 2430.5
| Bess Capacity Capacity Built (MW) | 1800 | 2200 | 1508 | 2500 | 1848 | 6000 | 3000
| Wind Capacity Capacity Built (MW) | 832.1 | 0 | 1188.4 | 641.9 | 1188.4 |  | 1188.4
CT—industrial frame | HD - 7F.05 - simple cycle Capacity Built (MW) | 717 | 956 | 717 | 956 | 717 | 717 | 717
| HD - 7HA.02 - simple cycle Capacity Built (MW) | 0
| LM2500+G4 - simple cycle Capacity Built (MW) | 0
| LM25200 22MW - simple cycle Capacity Built (MW) | 0
| HD - 7F.05 - combined cycle Capacity Built (MW) | 0
CC—single-shaft | HD - 7HA.02 - - combined cycle Capacity Built (MW) | 573 | 573 | 573 | 573 | 573 | 573 | 573
| LM2500+G4 - combined cycle Capacity Built (MW) | 0
| LM25200 22MW - combined cycle Capacity Built (MW) | 0
IC | Internal Combustion Capacity Built (MW) |  | 20 |  |  |  | 16
| CT_35MW Capacity Built (MW) | 0
CT_16MW | CT_16MW Capacity Built (MW) | 96 | 32 | 48 |  | 48 | 48 | 48
| Solar Utilisation (GWh) | 4634.9 | 7760.19 | 4241 | 6243.9 | 5911 | 8933.3 | 8933.3
| Bess Utilisation (GWh) | 1426.9 | 2751.23 | 1478.1 | 2394 | 2113.53 | 5070.8 | 2242.6
| Wind Utilisation (GWH) | 3098.6 | 0 | 3676.6 | 1468.1 | 3301.55 |  | 3301.55
CT—industrial frame | HD - 7F.05 - simple cycle Utilisation (GWh) | 1003.8 | 1946.08 | 1215.11 | 1599.3 | 734.09 | 1627.2 | 1086.2
| HD - 7HA.02 - simple cycle Utilisation (GWh) | 0
| LM2500+G4 - simple cycle Utilisation (GWh) | 0
| LM25200 22MW - simple cycle Utilisation (GWh) | 0
| HD - 7F.05 - combined cycle Utilisation (GWh) | 0
CC—single-shaft | HD - 7HA.02 - - combined cycle Utilisation (GWh) | 3071.2 | 2354.04 | 2657.76 | 2712.5 | 1979.55 | 1772.1 | 2213.7
| LM2500+G4 - combined cycle Utilisation (GWh) | 0
| LM25200 22MW - combined cycle Utilisation (GWh) | 0
IC | Internal Combustion Utilization (GWh) |  | 6.37 |  |  |  | 26.3
| CT_35MW Utilization (GWh) | 0
CT_16MW | CT_16MW Utilization (GWh) | 40.2 | 18.65 | 65.02 |  | 44.97 | 151.7 | 55.8
| Solar Capacity Factor (%) | 26.77% | 28.41% | 17.21% | 16.29% | 23.98% | 25.8% | 25.8%
| Bess Capacity Factor (%) | 9.049% | 14.28% | 11.19% | 10.93% | 13.06% | 9.648% | 8.533%
| Wind Capacity Factor (%) | 42.51% | 0% | 35.32% | 26.11% | 31.71% | 0% | 31.71%
CT—industrial frame | HD - 7F.05 - simple cycle Capacity Factor (%) | 15.98% | 23.24% | 19.35% | 19.1% | 11.69% | 25.91% | 17.29%
| HD - 7HA.02 - simple cycle Capacity Factor (%) | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| LM2500+G4 - simple cycle Capacity Factor (%) | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| LM25200 22MW - simple cycle Capacity Factor (%) | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| HD - 7F.05 - combined cycle Capacity Factor (%) | 0% | 0% | 0% | 0% | 0% | 0% | 0%
CC—single-shaft | HD - 7HA.02 - - combined cycle Capacity Factor (%) | 61.19% | 46.9% | 52.95% | 54.04% | 39.44% | 35.3% | 44.1%
| LM2500+G4 - combined cycle Capacity Factor (%) | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| LM25200 22MW - combined cycle Capacity Factor (%) | 0% | 0% | 0% | 0% | 0% | 0% | 0%
IC | Internal Combustion Capacity Factor (%) | 0% | 3.636% | 0% | 0% | 0% | 18.76% | 0%
| CT_35MW Capacity Factor (%) | 0% | 0% | 0% | 0% | 0% | 0% | 0%
CT_16MW | CT_16MW Capacity Factor (%) | 4.78% | 6.653% | 15.46% | 0% | 10.69% | 36.08% | 13.27%
| Installed Capacity (MW) | 5994.4 | 6898.9 | 6848.1 | 9045.8 | 7188.1 | 11306.6 | 9479
| Availlability (%) | 100% | 100% | 100% | 100% | 100% | 100% | 100%
| LCOE ($/MWh) | 83.4 | 79.3704 | 79.2062 | 98.0243 | 79.5887 | 112.743 | 91.0993
| CFE (%) | 69% | 70.8% | 70.47% | 70.09% | 80.41% | 79.65% | 81.18%
| Carbon Intensity lb/MWh | 193.5588 | 387.87 | 284.42 | 431.42 | 174.311 | 256.1368 | 168.8619
| Solar Curtainlment (GWh) | 39.61 | 500.56 | 282.89 | 590 | 479.21 | 1538.98 | 747.03
| Wind Curtailment (GWh) | 59.23 | 0 | 373.62 | 819 | 325.59 |  | 563.19
Note on B20: Abi-Rached, Habib (GE Vernova): is this utilisation? or #unit * MW?

## gas source
HD - 7F.05 - simple cycle | 239
HD - 7HA.02 - simple cycle | 376 | Note this unit was unit used in Google Study
LM2500+G4 - simple cycle |  | Not sure what is meant by LM2500 + G4?
LM25200 22MW - simple cycle |  | Not sure what is meant by LM2500 22 MW?
HD - 7F.05 - combined cycle | 372.41 | Note this unit was unit used in Google Study
HD - 7HA.02 - - combined cycle | 573
LM2500+G4 - combined cycle |  | Not sure what is meant by LM2500 + G4?
LM25200 22MW - combined cycle |  | Not sure what is meant by LM2500 22 MW?
LM 6000 simple cycle | 58.3
LM 2500 simple cycle | 34.5
Small GT 35 MW simple cycle | 35 | You can imply this model is an LM2500 simple cycle but it was not selected in our studies
Small GT 16 MW simple cycle | 16.5
Internal Combustion (IC) | 10
Bess | 100

## Location
High Solar - High Wind | High Solar - Low Wind | Low Solar - High Wind | Low Solar - Lower Wind
TX | AZ | ID | PA
Please populate these with the the state, or parts of the world, such as TX, TN, CA, …. All 52 states
Only possible to include the 4 sites we considered in the study