## FINAL
RE target - 70% of more
| High Solar High Wind ( TX) |  |  |  | High Solar Low Wind ( AZ) |  |  |  | Low Solar High Wind ( ID) |  |  |  | Low Solar Low Wind ( PA) |  |  |  | Scenario Profile | CC-Single Shaft | CT-Industrial, 35MW, 16 MW | Solar PV | Wind | Battery | RE %
Builds | Units | MW % | CF % | MWs | Units | MW % | CF | MWs | Units | MW % | CF | MWs | Units | MW By % | CF | MWs | High Solar / High Wind | 8.315% | 11.8% | 39.2% | 13.87% | 26.82% | 79.89%
CC—single-shaft | 1 | 8.315% | 73.52 | 573 | 1 | 10.2% | 75.08% | 573 | 1 | 8.367% | 80.83% | 573 | 1 | 8.708% | 74% | 573 | High Solar / Low Wind | 10.2% | 15.26% | 46% | 0% | 26% | 72%
CT—industrial frame | 3 | 10.4% | 18.21 | 717 | 4 | 17.02% | 43.62% | 956 | 3 | 10.47% | 33.84% | 717 | 4 | 14.53% | 25% | 956 | Low Solar / High Wind | 8.367% | 54.47% | 41.09% | 17.35% | 22.02% | 80.46%
CT_35MW | [16 empty] | Low Solar / Low Wind | 8.708% | 79.89% | 49.18% | 7.172% | 20.41% | 76.76%
CT_16MW | 6 | 1.393% | 0.72 | 96 | 2 | 0.5698% | 0.08% | 32 | 3 | 0.7009% | 0.51% | 48
IC |  |  |  |  | 1 | 0.1781% | 0.06% | 10
Wind |  | 13.87% | 41.15 | 955.81 |  | 0% | 0% | 0 |  | 17.35% | 36.95% | 1188.4 |  | 7.172% | 27.25% | 471.92
Solar PV with tracking |  | 39.2% | 25.27 | 2701.69 |  | 50.08% | 28.3% | 2812.39 |  | 41.09% | 16.95% | 2813.67 |  | 49.18% | 16.74% | 3236.32
Battery storage |  | 26.82% | 12.55 | 1847.98 |  | 21.95% | 25.58% | 1232.45 |  | 22.02% | 12.95% | 1508.06 |  | 20.41% | 32.84% | 1342.72
Total |  | 100% |  | 6891.48 |  | 100% |  | 5615.84 |  |  |  | 6848.13 |  | 100% |  | 6579.96
Non Renewables | 20.11% |  |  |  | 27.8% |  |  |  | 19.54% |  |  |  | 23.24%
Renewables % By Capacity | 79.89% |  |  |  | 72.03% |  |  |  | 80.46% |  |  |  | 76.76%
CFE % ( Energy) | 70.3% |  |  |  | 62.2% |  |  |  | 61.15% |  |  |  | 56%
Carbon Intensity | 361 |  |  |  | 436 |  |  |  | 465 |  |  |  | 560
LCOE to serve Data Center Load | ? |  |  |  | ? |  |  |  | ? |  |  |  |  | ?
LCOE_Including Battery loads | ? 61 |  |  |  | ? |  |  |  | ? |  |  |  |  | ?
Realibility | 100% |  |  |  | 99.97% |  |  |  | 99.99% |  |  |  | 99.97%
Total Generation Energy GWh | 14085 |  |  |  | 17156 |  |  |  | 13333 |  |  |  | 13299.28
EUE ( GWh) | 0 |  |  |  | 0 |  |  |  | 0.72 |  |  |  | 4
Carbon Intensity | 281 |  |  |  | 485 |  |  |  | 380 |  |  |  | 564
EUE hours | 0 |  |  |  | 0 |  |  |  | 3 |  |  |  | 18
| GWh_Curtailed | GWH_Produced | % |  | GWh_Curtailed | GWh_Produced | % |  | GWh_Curtailed | GWh | % |  | GWh_curtailment | GWh | %
Total Curtailment | 804.8 | 9212.55 | 8.034%
Wind | 325.59 | 3301.55 | 8.976% | [5 empty] | 373 | 3676.59 | 9.211% |  | 56.48 | 1135 | 4.74%
Solar | 479.21 | 5911 | 7.499% |  | 737 | 6713.96 | 10.98% |  | 282 | 4240.99 | 6.235% |  | 197 | 4832 | 3.917%
SC Ratio Threshold >1.26 |  |  |  | 0.78332 |  |  |  | 1.0187 |  |  |  | 0.71588 |  |  |  | 0.7726
RE target -80% of more
| High Solar High Wind ( TX) |  |  |  | High Solar Low Wind ( AZ) |  |  |  | Low Solar High Wind ( ID) |  |  |  | Low Solar Low Wind ( PA)
Builds | Units | MW % | CF % | MWs | Units | MW % | CF | MWs | Units | MW % | CF | MWs | Units | MW By % | CF | MWs
CC—single-shaft | 1 | 7.987% | 70.19 | 573 | 1 | 10.22% | 74.5 | 573 | 1 | 8.309% |  | 573 | 1 | 8.372% | 87.18 | 573
CT—industrial frame | 3 | 9.994% | 20.01 | 717 | 4 | 17.05% | 51.2 | 956 | 3 | 10.4% |  | 717 | 4 | 13.97% | 55.54 | 956
CT_35MW | 0 | 0% | 0 | 0 | 3 | 1.873% | 0.39 | 105 | 2 | 1.015% |  | 70 | 0 | 0% | 0 | 0
CT_16MW | 10 | 2.23% | 0.78 | 160 | 0 | 0% | 0 | 0 | 1 | 0.232% |  | 16 | 3 | 0.7013% | 0.09 | 48
Wind |  | 14.36% | 41.14 | 1030.51 |  | 0% | 0 | 0 |  | 27.67% |  | 1908.03 |  | 10.39% | 27.28 | 711.08
Solar PV with tracking |  | 40.45% | 24.98 | 2901.9 |  | 52.16% | 28.21 | 2924.06 |  | 26.9% |  | 1855.07 |  | 46.63% | 16.74 | 3191.61
Battery storage |  | 24.98% | 13.26 | 1792.1 |  | 21.76% | 40.83 | 1219.94 |  | 25.48% |  | 1757.03 |  | 19.94% | 43.59 | 1364.7
Total |  | 100% |  | 7174.51 |  | 100% |  | 5605.84 |  | 100% |  | 6896.13 |  | 100% |  | 6844.39
Non Renewables |  | 20.21% |  |  |  | 29.15% |  |  |  | 19.95% |  |  |  | 23.04%
Renewables % By Capacity | 79.79% |  |  |  | 73.92% |  |  |  | 80.05% |  |  |  | 76.96%
CFE % ( Energy) | 72% |  |  |  | 59% |  |  |  | 66% |  |  |  | 56%
Carbon Intensity | 271 |  |  |  | 505 |  |  |  | 356 |  |  |  | 557
LCOE to serve Data Center Load | 77 |  |  |  | 69 |  |  |  | 84 |  |  |  | 81
LCOE_Including Battery loads | 64 |  |  |  | 60 |  |  |  | 75 |  |  |  | 73
Realibility | 100% |  |  |  | 100% |  |  |  | 100% |  |  |  | 99.99%
Total Generation Energy GWh | 14201 |  |  |  | 13821 |  |  |  | 13344 |  |  |  | 13326
EUE ( GWh) | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0.75
EUE hours | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 3
| GWh_Curtailed | GWH_Produced | % |  | GWh_Curtailed | GWh_Produced | % |  | GWh_Curtailed | GWH_Produced | % |  | GWh_Curtailed | GWH_Produced | %
Total Curtailment |  |  |  |  | 139 | [5 empty] | 13% |  | 278.92
Wind | 88.23 | 1706.99 | 4.915% |  | 0 | 0 | 0 |  | 857.7 | 5645.08 | 13.19% |  | 88.23 | 1706.99 | 5.169%
Solar | 190.69 | 4769.75 | 3.844% |  | 952.72 | 6794.47 | 14.02% |  | 361.43 | 2621.18 | 12.12% |  | 190.69 | 4769.75 | 3.998%
SC Ratio | 0.72856 |  |  |  | 0.9798 |  |  |  | 0.76134 |  |  |  | 0.73411
Scenarios
100% RE - HSHW-TX
Builds | MWs |  | CF %
Wind | 1520.95 |  | 23
Solar PV with tracking | 7298.73 | 7298.73 | 14.47
Battery storage | 8648.89 | 8648.89 | 5.35
Total | 17468.57 | 15947.62
Non Renewables | 0%
Renewables % By Capacity | 100%
CFE % ( Energy) | 100%
Carbon Intensity | 0
LCOE to serve Data Center Load | 143.88
LCOE_Including Battery loads | 124.33
Realibility | 100%
Total Generation Energy GWh | 16364.09
EUE ( GWh) | 0
EUE hours | 0
| GWh_Curtailed | GWH_Produced | %
Total Curtailment | 10727 | 16364 | 47%
Wind | 2712.95 | 3058.8
Solar | 8014.19 | 9249.25
SC Ratio | 0
70%RE with 6 hrs BESS
High Solar High Wind ( TX)
Builds | Units | MW % | CF % | MWs
CC—single-shaft | 1 | 8.327% | 71.21 | 573
CT—industrial frame | 3 | 10.42% | 12.72 | 717
CT_35MW | 0 | 0% | 0 | 0
CT_16MW | 0 | 0% | 0 | 0
Wind |  | 14.04% | 41.15 | 966.03
Solar PV with tracking |  | 42.31% | 25.44 | 2911.26
Battery storage- 6 Hrs |  | 24.91% | 16.47 | 1713.9
Total |  | 100% |  | 6881.19
Non Renewables | 18.75%
Renewables % By Capacity | 81.25%
CFE % ( Energy) | 74%
Carbon Intensity | 244.29
LCOE to serve Data Center Load | 73.45
LCOE_Including Battery loads | 61.63
Realibility | 100%
Total Generation Energy GWh | 14149.8
EUE ( GWh) | 0
EUE hours | 0
| GWh_Curtailed | GWH_Produced | %
Total Curtailment | 1188.95 | 14149.75 | 7.751%
Wind | 424.99 | 3240.94
Solar | 763.96 | 6121.93
SC Ratio | 0.73892

## Supply Stack
| High Solar High Wind ( TX) |  |  |  | High Solar Low Wind ( AZ) |  |  |  | Low Solar High Wind ( ID) |  |  |  | Low Solar Low Wind ( PA)
Builds | Units | MW % | CF | MWs | Units | MW % | CF | MWs | Units | MW % | CF | MWs | Units | MW By % | CF | MWs
CC—single-shaft
CT—industrial frame
CT_35MW
CT_16MW
Wind
Solar PV with tracking
Battery storage
Total

## Build_RE%
| High Solar High Wind ( TX) | High Solar Low Wind ( AZ) | Low Solar High Wind ( ID) | Low Solar Low Wind ( PA)
Builds | MWs | MWs | MWs | MWs
CC—single-shaft
Wind
Solar PV with tracking

## Carbon Intensity
| High Solar High Wind ( TX) | High Solar Low Wind ( AZ) | Low Solar High Wind ( ID) | Low Solar Low Wind ( PA)
Carbon Intensity Lb/MWh | 281 | 485 | 380 | 564
Carbon Intensity Lb/MWh
High Solar High Wind (TX) | 281
High Solar Low Wind (AZ) | 485
Low Solar High Wind (ID) | 380
Low Solar Low Wind (PA) | 564

## SC Ratio
| High Solar High Wind ( TX) | High Solar Low Wind ( AZ) | Low Solar High Wind ( ID) | Low Solar Low Wind ( PA)
Total | 5210.8 | 5107.98 | 4638.69 | 5797.733
Thermal Capacity | 28.79% | 28.94% | 30.07% | 31.65%
Renewables % By Capacity | 72.79% | 72.83% | 71.82% | 70.27%
Carbon Free Energy CFE% | 59% | 58.1% | 49% | 42.5%
Carbon Intensity lb/MWh | 361 | 436 | 465 | 560
Overall System Reliability % | 100% | 99.97% | 99.97% | 100%
SC Ratio | 373.62 | 373.62 | 373.62 | 373.62
| 282.89 | 282.89 | 282.89 | 282.89

## LCOE
LCOE $/MWh | High Solar High Wind (TX) | High Solar Low Wind (AZ) | Low Solar High Wind (ID) | Low Solar Low Wind (PA) | Thermal Only
Total System w/ BESS Load | 63 | 59 | 72 | 73 | 79.4916
Total System w/o BESS Load | 75 | 68 | 79 | 80 | 79.4916
Total System for DC load ( 75% system )

## RE Curtailment
| High Solar High Wind ( TX) |  |  |  | High Solar Low Wind ( AZ) |  |  | Low Solar High Wind ( ID) |  |  | Low Solar Low Wind ( PA)
| GWh_Curtailed | GWH_Produced | % |  | GWh_Curtailed | GWh_Produced | % | GWh | GWh | % | GWh | GWh | %
Total Curtailment | 12.1 |  |  |  | 139 |  |  |  | 8.6 |  | 1.04
Wind | 5.78 | 3335.35 | 0.1733% |  |  |  |  | 3634.5 | 4.62 | 0.1271% | 0.5 | 474.95 | 0.1053%
Solar | 6.32 | 3284.31 | 0.1924% |  | 139 | 6153 | 2.259% | 1800 | 3.98 | 0.2211% | 0.6 | 3878.12 | 0.01547%
|  |  | Wind | Solar
| High Solar High Wind (TX) | GWh_Curtailed | 5.78 | 6.32
|  | GWH_Produced | 3335.35 | 3284.31
|  | % Curtailed | 0.1733% | 0.1924%
| High Solar Low Wind (AZ) | GWh_Curtailed | 0 | 139
|  | GWH_Produced | 0 | 6153
|  | % Curtailed |  | 2.259%
| Low Solar High Wind (ID) | GWh_Curtailed | 3634.5 | 1800
|  | GWH_Produced | 4.62 | 3.98
|  | % Curtailed | 0.1271% | 0.2211%
| Low Solar Low Wind (PA) | GWh_Curtailed | 0.5 | 0.6
|  | GWH_Produced | 474.95 | 3878.12
|  | % Curtailed | 0.1053% | 0.01547%